# Engineering Specification

# Model E Alarm Check Valve with E3 Trim

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-Pipe Sprinkler Systems (formerly 13930)

Alarm Check Valve shall be [cULus Listed] [FM Approved] for use in wet-pipe fire protection systems for installation in the vertical or horizontal position.  The Alarm Check Valve shall be a straight flow design, check type valve with grooved seat design. The Alarm Check Valve shall have a rated working pressure of 175 psi (12.1 bar) and shall be factory hydrostatic tested at 350 psi (24.2 bar). Valve size shall be [4” (100mm)] [6” (150mm)] [8” (200mm)] with [US Standard flanged inlet and outlet flanges per ANSI B 16.1 (125 lb)] [US Standard flanged inlet per ANSI B 16.1 (125 lb) and grooved outlet per ANSI/AWWA C606] [Metric flanged inlet and outlet].  Valve construction shall be [for 4” valve: cast iron] [for 6” & 8” valves: ductile iron] with bronze seat.  The Alarm Check Valve trim shall be galvanized with [constant pressure closed drain, including external bypass trim] [variable pressure closed drain, including external bypass and retard chamber] [variable pressure open drain, including external bypass and retard chamber]. Alarm check valve trim shall include a non-silenceable alarm connection for the waterflow pressure switch and shall be configured to cause the clapper to open when testing alarm line devices. {Optional: A [cULus Listed] [FM Approved] pressure relief valve trim kit shall be provided.} [Optional: A Test & Drain valve trim kit shall be provided.]

Alarm Check Valve shall be the Reliable Model E with Model E3 trim. Refer to Reliable Bulletin 417 for associated information.