# Engineering Specification

# Model F1FR-SS Series Stainless Steel Quick Response

# Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, standard spray [upright] [pendent] that is [cULus Listed] [FM Approved] as Corrosion Resistant. Sprinkler frame and deflector shall be of Type 316 stainless-steel alloy having a [½” NPT] [¾” NPT] thread.  Water seal assembly shall consist of a 3 mm glass bulb operating element and beryllium-nickel sealing washer with PTFE tape on both sides. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [175F (79C)] [200F (93C)] [286F (141C)]. Sprinklers shall have a nominal K-factor of [5.6 gpm/psi1/2 (81 l/min/bar1/2) – standard orifice] [8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice]. Sprinklers shall have a rated working pressure of 175 psi (12.1 bar).  Standard finish: [None] [White Polyester] [Black Polyester] [Custom Color Polyester].

Sprinklers shall be of the Model F1FR-SS Series Stainless Steel Sprinklers. Refer to Reliable Bulletin 065 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed pendent sprinklers, add:

{Two-piece stainless-steel recessed escutcheon assembly shall be a factory-assembled, push-on/thread-off design with ½” adjustment. Standard finish: [None] [White Polyester] [Black Polyester] [Custom Color Polyester]} {Two-piece stainless-steel recessed escutcheon assembly shall be a factory-assembled, “friction-fit” design with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [None] [White Polyester] [Black Polyester] [Custom Color Polyester]} {One-piece escutcheon shall be stainless steel. Standard finish: [None] [White Polyester] [Black Polyester] [Custom Color Polyester].}

Escutcheons that are permitted by the manufacturer to be used with each Model F1FR-SS Series recessed sprinkler shall be used.