# Engineering Specification

# Model F1FR56-300 QREC Series Quick Response

# Extended Coverage Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, extended coverage pendent that is cULus Listed. Sprinkler frame and deflector shall be of bronze frame construction having a ½” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)].  Sprinklers shall have a nominal K-factor of 5.6 gpm/psi1/2 (81 l/min/bar1/2) – standard orifice. Sprinklers shall have a rated working pressure of 300 psi (20.7 bar).  Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be the Model F1FR56-300 QREC pendent, SIN RA3045. Refer to Reliable Bulletin 030 for additional sprinkler information.

For recessed pendent sprinklers, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [special finish – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ½” adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].}

Recessed escutcheons that are listed for use with the Model F1FR56-300 QREC recessed pendent sprinkler shall be used.

For concealed pendent sprinklers, add:

Concealed pendent sprinklers shall have a factory-installed, steel sprinkler cup. Method of attaching the cover plate to the sprinkler cup shall be a push-on and thread-off design allowing [1/2” (13 mm)] [5/8” (8 mm)] of adjustment. The cover plate temperature rating shall be 135F (57C). A factory applied protective cap shall be provided to protect against installation damage. Standard cover plate finish: [Chrome] [White] [Special finish– specify].

Cover plates used with the Model F1FR56-300 QREC concealed pendent shall be the Model CCP cover plate.