# Engineering Specification

# Model F1FR80 QREC Series Quick Response Extended Coverage Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, extended coverage [pendent] [horizontal sidewall] that is [cULus Listed] [FM Approved]. Sprinkler frame and deflector shall be of bronze frame construction having a ¾” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [SIN RA4862 only: 175F (79C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice. Sprinklers shall have a rated working pressure of [175 psi (12 bar)] [UL Listed only: 250 psi (17 bar)].  Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1FR80 QREC Series. Refer to Reliable Bulletin 148 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed sprinklers, add:

Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].

Recessed escutcheons that are listed for use with the Model F1FR80 QREC recessed sprinkler shall be used.

For concealed sprinkler, add:

Concealed cover plate shall be push-on/thread off with ½” (13 mm) adjustment. Standard finish: [White Paint] [Chrome Plated] [Special finish– specify].

Cover plates that are listed for use with the Model F1FR80 QREC concealed sprinkler shall be used.