# Engineering Specification

# Model GL112 Quick Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be quick response [upright] [pendent] sprinklers that are FM Approved. Sprinkler frame and deflector shall be of bronze construction, utilizing a levered fusible alloy solder link and having a [¾” NPT] [ISO 7-1R¾] thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer containing no plastic parts. Sprinkler temperature rating shall be [165F (74C)] [212F (100C)].  Sprinklers shall have a nominal K-factor of 11.2 gpm/psi1/2 (160 l/min/bar1/2) – extra-large orifice. Sprinklers shall have a rated working pressure of 175 psi (12 bar).

Sprinklers shall be of the Model GL112 Series. Refer to Reliable Bulletin 132 for associated sprinkler information.