# Engineering Specification

# Model J112SS Stainless Steel Extended Coverage

# Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a [quick] [standard] response, extended coverage [pendent] [upright] that is cULus Listed. Sprinkler frame and deflector shall be of Type 316 stainless steel construction having a [¾” NPT] [ISO 7-1R¾] thread.  Water seal assembly shall consist of a Beryllium-nickel alloy gold plated sealing washer per MIL-G-45204, Type 3, Class 2 with PTFE tape on both sides, and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [155F (68C)] [200F (93C)] [286F (141C)].  Sprinklers shall have a nominal K-factor of 11.2 gpm/psi1/2 (160 l/min/bar1/2) – extra large orifice. Sprinklers shall have a rated working pressure of 175 psi (12 bar).  Standard finish: [None] [White Polyester] [Black Polyester] [Custom Color Polyester – Specify].

Sprinklers shall be of the Model J112SS Stainless Steel Series. Refer to Reliable Bulletin 178 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed sprinklers, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of Type 316 stainless steel alloy construction, push-on and thread off design with ½” adjustment. Standard finish shall be [None] [White Polyester] [Black Polyester] [Custom Color Polyester – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon of Type 316 stainless steel alloy construction, with ¾”(19 mm) adjustment. Standard finish: [None] [White Polyester] [Black Polyester] [Custom Color Polyester – specify].}

Recessed escutcheons that are listed for use with the Model J112SS recessed sprinkler shall be used.

For Specific Application Criteria for Use Under Concrete Tee Construction, add:

Pendent and upright sprinklers shall be cULus Listed for installation under concrete tee construction in accordance with the following specific application criteria:

- Max. Tee Depth: 2’- 6” (0.8m)

- Max. Tee Stem Spacing: 7’- 6” (2.3m)

- Min. Tee Stem Spacing: 3’- 0” (0.9m)

- Max. Tee Length: 32’- 0” (9.8m) or baffles not less than the depth of the tees must be installed so that the longitudinal space between baffles does not exceed 32ft (9.8m) in length.

- Max. Deflector distance below Tee: 1” (25mm)

- Comply with obstructions to the Sprinkler Discharge Pattern Development requirements of the NFPA13 where deflector is located above bottom of tee.