# Engineering Specification

# Model N252EC Pendent Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be [cULus Listed standard response] [FM Approved quick response], control mode density/area (CMDA) extended coverage pendent sprinklers for storage and non-storage applications in accordance with the design requirements of [NFPA 13] [FM Global Data Sheets]. The sprinkler shall be approved for use as a control mode specific application (CMSA) sprinkler in accordance with [the Alternative Sprinkler Systems Design chapter for NFPA 13] [FM Global Data Sheet 8-9]. Sprinklers shall be approved for use in extended coverage in-rack sprinkler systems in accordance with NFPA 13 and FM Data Sheet 8-9.  Sprinklers shall offer a maximum coverage area of 14 ft. x 14 ft. (4.3 m x 4.3 m) and have a nominal K-factor of 25.2 gpm/psi1/2 (360 l/min/bar1/2) and [1” NPT] [ISO7 R-1] threaded end connections. Sprinklers shall have a rated working pressure of 175 psi (12 bar). Sprinkler temperature rating shall be [Ordinary 165ºF (74ºC)] [Intermediate 212ºF (100ºC)]. Sprinkler frame and deflector to be of bronze construction. Fusible alloy solder link assembly shall utilize the strut and lever principle of operation with approved fast response beryllium-nickel thermal element with protective [black painted, 165ºF (74ºC)] [gray painted, 212ºF (100ºC)] coating. Water seal shall consist of a Teflon-coated Bellville spring washer and brass cap assembly containing no plastic parts. Response Time Index (RTI) shall be less than 50 ms1/2.

{For recessed pendent sprinklers, add (cULus only): Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [special finish – specify].}

Extended coverage pendent sprinklers shall be Reliable Model N252EC, SIN RA0842. Refer to Reliable Bulletin 008 for associated sprinkler information.