# Engineering Specification

# Model TD Test and Drain Valve

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-Pipe Sprinkler Systems (formerly 13930)

The test and drain valve shall be a [cULus Listed] [FM Approved] one-piece, cast brass, integral single-handle, tri-position test and drain ball valve allowing both testing of the waterflow alarm and draining of the wet-pipe fire protection system. The test and drain valve shall be for horizontal or vertical installation. Nominal valve size shall be [1” (25mm)] [1¼” (40 mm)] [2” (50 mm)] with [NPT (ISO7-1) threaded] [available with 1¼” & 2” only: C606 grooved] inlet connection and NPT (ISO7-1) threaded outlet connection.

The valve shall include a sight glass and [2.8 (40)] [4.2 (60)] [5.6 (80)] [8.0 (115)] [11.2 (160)] [16.8 9240)] K-factor test orifice size.  The tri-position ball valve handle shall have an optional tamper resistant lock out feature.  A built-in drain port shall be available to permit hydrostatic testing without draining the system.  Valve shall have a working pressure rating of 300 psi (20.7 bar).  A tap for an optional ½” pressure relief valve kit shall be provided. {Optional: Test & Drain valve shall be provided with a pressure relief valve trim kit with [175 psi (12.1 bar)] [185 psi (12.8 bar)] [210 psi (14.5 bar)] [260 psi (17.9 bar)] [310 psi (21.4 bar)] rating.}

The test and drain valve shall be the Reliable Model TD Test and Drain Valve. Refer to Reliable Bulletin 618 for associated information.