# Engineering Specification

# Residential Riser Assembly

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-Pipe Sprinkler Systems (formerly 13930)

Residential Riser Assembly shall be cULus approved for horizontal or vertical installation as a one-piece, factory assembled unit for use in NFPA 13D and 13R residential systems.  The riser manifold assembly shall consist of a [1” (25mm)] [1-1/2” (40 mm)] [2” (50 mm)] cast, non-welded stainless steel body with [available for 1” only: male NPT threaded] [female NPT threaded] [available for 1½” only: grooved] end connections.

The manifold piping shall contain cast-on lettering clearly identifying manifold pipe size, flow direction, cULus Listing, and the test and drain outlet.  A built-in drain port shall be available to permit hydrostatic testing without draining the system.  Assembly shall have a working pressure rating of 175 psi (12.1 bar).  Cast mounting holes shall be provided for recessed or flush mounting to wall.  For stud mounting, a support bracket shall be provided specifically designed for the cast mounting holes.

Basic Trim

[Residential riser manifold assembly trim shall include a 3-way valve and associated cULus Listed pressure gauge, a drain valve, and dedicated waterflow detector containing two sets of SPDT (Form C) contacts, having an electrical rating of 10A @ 125/250 VAC/2.5 A @ 24VDC.]

Basic Trim with Test & Drain Valve

[Residential riser manifold assembly trim shall include a 3-way valve and associated cULus Listed pressure gauge, a Test & Drain valve, and a dedicated waterflow detector containing two sets of SPDT (Form C) contacts, having an electrical rating of 10A @ 125/250 VAC/2.5 A @ 24VDC.  The test orifice size for the Test & Drain assembly shall be 3/8” (10 mm), 7/16” (11 mm) or ½” (15 mm).]

Basic Trim with Test & Drain Valve with Pressure Relief Valve Trim Kit

{Residential riser manifold assembly trim shall include a 3-way valve and associated cULus Listed pressure gauge, a Test & Drain valve, and dedicated waterflow detector containing two sets of SPDT (Form C) contacts, having an electrical rating of 10A @ 125/250 VAC/2.5 A @ 24VDC.  Pressure relief valve trim kit with [175 psi (12.1 bar)] [185 psi (12.8 bar)] [210 psi (14.5 bar)] [260 psi (17.9 bar)] [310 psi (21.4 bar)] rating shall be provided.}

Residential Riser Assembly shall be the Reliable Residential Riser. Refer to Reliable Bulletin 425 for associated information.